## ReadMe
add-device bulk template
Fill the sheets, then run: python .claude/skills/add-device/scripts/excel_to_devices.py <this file> --check
General
One row per device in Devices; one row per tag in the protocol sheet; link them with device_id.
Rows whose first cell starts with # are comments/examples and are skipped (the grey rows).
Blank cell = use the model default. TODO = unknown: the tag is left out and reported (host / unit_id / endpoint_url get a visible placeholder and the device is forced to enabled: false).
Never type a secret: *_env columns hold environment variable NAMES (e.g. HUB_OPCUA_PLC02_PASSWORD).
Names (device_id, site, area, tag) = lowercase ASCII snake_case, starting with a letter.
Every tag is read-only unless access = read_write, which also needs min and max (control-safety rules apply).
Devices
Always: device_id, name, protocol, site, area. poll_interval_ms: modbus_tcp/opcua only.
modbus_tcp: host, unit_id (+ optional port, timeout_ms, retries, byte_order, word_order, max_registers_per_read).
mqtt: broker_ref (must exist in config/brokers.yaml), telemetry_topic (+ command_topic, status_topic, qos).
opcua: endpoint_url, security_policy, security_mode, auth_type (+ username_env/password_env, namespace, client_certificate_env, client_private_key_env, timeout_ms). Secure policies need both client_*_env.
ModbusRegisters
address_style: protocol (0-based, default) ¦ one_based (address-1) ¦ modicon (40001-style, 5 or 6 digits; register_type is derived from the first digit).
register_type: coil ¦ discrete_input ¦ holding ¦ input (not needed for modicon).
count: only for data_type string (registers, 2 chars each). 32-bit order is per device (byte_order/word_order).
MqttTags / OpcuaTags
json_path examples: $.data.temp, $['key with space'], $.values[0]. node_id examples: ns=2;s=Pump1.Speed, ns=3;i=1042.
Tag columns
data_type: bool int16 uint16 int32 uint32 float32 float64 string. engineering = raw * scale + offset.

## Devices
device_id | name | protocol | site | area | enabled | description | poll_interval_ms | host | port | unit_id | timeout_ms | retries | byte_order | word_order | max_registers_per_read | broker_ref | telemetry_topic | command_topic | status_topic | qos | endpoint_url | security_policy | security_mode | auth_type | username_env | password_env | namespace | client_certificate_env | client_private_key_env
# meter_99 | Example meter (row ignored) | modbus_tcp | kish | substation | TRUE | Rows starting with # are skipped | 1000 | 192.168.10.99 | 502 | 1 | 1000 | 3 | big | little | 100
meter_03 | Gate feeder meter | modbus_tcp | kish | gate |  |  | 2000 | 192.168.10.23 |  | 1 |  |  |  | little | 60
vfd_01 | Pump 1 drive | modbus_tcp | kish | pump_station |  |  |  | TODO |  | 3
gate_counter_01 | Gate vehicle counter | mqtt | kish | gate | [11 empty] | plant_broker | kish/gate/counter_01/data |  |  | 1
env_sensor_03 | Cold room sensor | mqtt | kish | warehouse | [11 empty] | plant_broker | kish/warehouse/env_sensor_03/telemetry
plc_02 | Booster pump PLC | opcua | kish | pump_station |  |  | 500 | [13 empty] | opc.tcp://192.168.10.51:4840 | None | None | anonymous

## ModbusRegisters
device_id | tag | description | unit | data_type | address_style | register_type | address | count | scale | offset | min | max | access
# meter_99 | voltage_l1 | Phase 1 voltage | V | float32 | modicon |  | 30001
# meter_99 | demand_limit | Writable example | kW | uint16 | protocol | holding | 100 |  |  |  | 0 | 500 | read_write
meter_03 | voltage_l1 |  | V | float32 | modicon |  | 30001
meter_03 | active_power |  | kW | float32 | modicon |  | 30013
meter_03 | relay | Relay coil |  | bool | modicon |  | 00001 | [5 empty] | read_write
meter_03 | demand_limit |  | kW | uint16 | modicon |  | 40101 |  | 0.1 |  | 0 | 500 | read_write
meter_03 | frequency |  | Hz | float32 | modicon |  | TODO
vfd_01 | motor_speed |  | rpm | int16 | one_based | holding | 1
vfd_01 | output_current |  | A | uint16 | one_based | holding | 2 |  | 0.01

## MqttTags
device_id | tag | description | unit | data_type | json_path | scale | offset | min | max | access
# sensor_99 | temperature | Air temperature | degC | float32 | $.data.temp |  |  | -20 | 60
gate_counter_01 | vehicle_count |  |  | uint32 | $.count
gate_counter_01 | barrier_open |  |  | bool | $['barrier state']
env_sensor_03 | temperature |  | degC | float32 | $.data.temp |  |  | -40 | 85

## OpcuaTags
device_id | tag | description | unit | data_type | node_id | scale | offset | min | max | access
# plc_99 | motor_speed | Motor speed | rpm | float32 | ns=2;s=Pump1.MotorSpeed
plc_02 | motor_speed |  | rpm | float64 | ns=2;s=Pump2.Speed
plc_02 | motor_running |  |  | bool | ns=2;i=1042